CAMERA & SERVER INFRASTRUCTURE SPECIFICATION

Clinker Bucket Elevator Vision Monitoring System

MVP: direct NVR Ethernet and physical Ubuntu server

Document Status: Draft v0.7 — revised to match the approved MVP baseline

| Version | Change |
| --- | --- |
| 0.7 | Replaced VMware/OT/fibre/NAS assumptions with a physical HP server, private NVR Ethernet connection, local HDD evidence, and temporary Internet only for installation. |

# 1 Purpose and confirmed baseline

This document records the hardware, network, storage, and installation assumptions for the MVP. Values marked TBC must be recorded during commissioning; this document must not invent IP addresses or credentials.

| Item | Current baseline | Status |
| --- | --- | --- |
| NVR | Dahua network video recorder; label appears to show NVR4232-EI | Verify exact model in web UI |
| Cameras | Six cameras connected to the NVR | Confirmed |
| MVP camera | CAM-1 / channel 1 / godet view | Confirmed |
| Camera source | NVR channel RTSP, not direct camera IP | Confirmed design |
| Server | Physical HP server, approximately 2015 | Confirmed |
| Memory | 16 GB RAM | Reported; verify |
| CPU | Xeon approximately 2.40 GHz | Exact model TBC |
| Disk | 500 GB local HDD | Reported; verify free space/health |
| Operating system | Ubuntu Server LTS | Installed; record version |
| Model location | Same physical server in Docker | Confirmed design |
| Evidence storage | Local server disk | MVP decision |

# 2 Camera inventory

| ID | Target | Phase | MVP state |
| --- | --- | --- | --- |
| CAM-1 | Godets, line 1 | MVP | Enabled |
| CAM-2 | Godets, line 2 | Future | Disabled |
| CAM-3 | Galets, line 1 | Future | Disabled |
| CAM-4 | Galets, line 2 | Future | Disabled |
| CAM-5 | Clinker level/spillage | Future | Disabled |
| CAM-6 | Reserve/expansion | Future | Disabled |

The project documents currently record 2688×1520 at 25 fps, no infrared, and day/night capability for the cameras. These values should be verified from the NVR/camera configuration before performance testing.

# 3 Network topology

CAM-1 ... CAM-6 -> Dahua NVR --private Ethernet--> Ubuntu server

Ubuntu server --temporary approved Internet--> package/image installation only

The NVR is not assumed to be on the plant OT network.

The NVR-to-server link should be a private or otherwise controlled network segment.

The NVR IP, server IP, subnet, gateway, and interface names are deployment values and must be recorded during commissioning.

Internet is required only to install Ubuntu packages and obtain Docker images, unless images are delivered by USB/offline media.

After installation, disconnect or disable the temporary Internet connection.

The web viewer must bind to localhost so it is usable on the server without becoming a remote service.

# 4 Server requirements

| Resource | MVP requirement/recommendation |
| --- | --- |
| CPU | Xeon 2.40 GHz or better; record exact model. Benchmark the real model before accepting the sample interval. |
| RAM | 16 GB installed. Reserve enough memory for Ubuntu, Docker, pipeline, model, and filesystem cache. |
| Disk | 500 GB local HDD. Use separate directories for application data, SQLite, evidence, logs, and image archives. |
| OS | Ubuntu Server LTS; keep security updates enabled during the test period. |
| Docker | Docker Engine and Docker Compose plugin. |
| Display | Local monitor/keyboard or approved console access for operators and maintenance. |
| Network | At least one interface for the private NVR link; a temporary Internet path may use a second interface or an approved temporary change. |

# 5 Local storage

| Data | Location | Policy |
| --- | --- | --- |
| SQLite alerts | /srv/clinker-vision/data/alerts.db | WAL mode; local only. |
| Evidence JPEGs | /srv/clinker-vision/evidence/YYYY/MM/DD/CAM-1/ | Full-frame overlay; quality 85; 365-day target. |
| Configuration | /srv/clinker-vision/config/ | Permissions 600; never commit credentials. |
| Docker images | /srv/clinker-vision/images/ | Keep exact versioned offline archives during commissioning. |
| Logs | /srv/clinker-vision/logs/ or Docker logs | Rotate to prevent disk exhaustion. |

At an estimated 800 KB–1 MB per evidence image, a 500 GB disk is substantially larger than the MVP's one-year evidence requirement. Actual alert rate and free-space monitoring must still be measured. No NAS/NFS share is required for the MVP.

# 6 Installation checklist

Record the server hostname, Ubuntu version, exact CPU, RAM, disk health, and network interfaces.

Connect the NVR and server through the approved Ethernet arrangement.

Obtain the NVR IP and verify the web interface from the server.

Verify CAM-1 preview and obtain the channel-1 RTSP URL.

Install Docker and Docker Compose while temporary Internet is available.

Load the pipeline and model images from the release package.

Configure the protected NVR credentials and CAM-1 URL.

Start the Compose stack and verify model, NVR, SQLite, evidence, and local web viewer.

Disconnect Internet and repeat the verification.

Record image tags/digests and complete the deployment sign-off.

# 7 Capacity and performance checks

| Check | Acceptance evidence |
| --- | --- |
| NVR connectivity | Stable CAM-1 RTSP connection for a continuous test period. |
| Frame sampling | Observed sample interval approximately two seconds. |
| Model throughput | CPU benchmark from model owner and local end-to-end measurement. |
| Disk | Evidence growth rate, free space, and cleanup behavior recorded. |
| Thermal | Server temperature and fan behavior acceptable for the test period. |
| Offline operation | Stack restarts and runs after Internet is removed. |

# 8 Infrastructure open items

| ID | Item | Owner |
| --- | --- | --- |
| INF-1 | Exact NVR model, firmware, IP, credentials, codec, and CAM-1 RTSP URL. | Project/plant |
| INF-2 | Exact HP server model, CPU model, disk health, hostname, and static IP. | Project owner |
| INF-3 | Confirm whether the server has one or two network interfaces and define the temporary Internet method. | Project/IT |
| INF-4 | Run CPU/model benchmark on the real server. | Project/model owner |
| INF-5 | Confirm local disk cleanup and alert retention after real alert-rate measurement. | Project owner |
| INF-6 | Define physical access and operator console location. | Plant/project |